## Hal.14 List FT
DATA SHEET
FLOW TRANSMITTER
INSTRUMENT LIST :
No | Tag. Number | Type |  | Q'ty | Service | Element Type | Fluid | Line / Equipment No. | PID No. | Location | Line Size | Process Conditions | [9 empty] | Page
[12 empty] | Fluid | Flow (m3/h) |  |  | Oper. Press. (bar) |  |  | Oper. Temp. (°C)
[13 empty] | Min | Nor | Max | Min | Nor | Max | Min | Nor | Max
1 | FT 1210~1220 | Flow Transmitter |  | 6 | FLOW INLET MAIN CW COPPER COOLER | Magnetic | Soften Water | 2800 | P3FH-PR-2800-PID-1001 | System 2 | DN 150 sch 40 | water | 0 | 9 | 18 | 0 | 3.5 | 7 | 0 | 45 | 100 | 15
2 | FT 1001~1176 | Flow Transmitter |  | 56 | MAIN HEADER CW/RW COPPER COOLER | Magnetic | Soften Water | 2800 | P3FH-PR-2800-PID-1001 | System 2 | DN 25 sch 40 | water | 0 | 9 | 18 | 0 | 3.5 | 7 | 0 | 45 | 100 | 15
3 | FT 2001 | Flow Transmitter |  | 1 | FLOW TRANSMITTER FOR SLAG GRANULATION | Magnetic | Sea Water | 2500 | P3FH-PR-2500-PID-1001 | System 2 | DN 200 sch 40 | water | 0 | 300 | 600 | 0 | - | 3 | 30 | 45 | 60 | 15

## Hal. 15FT
DATA SHEET
FLOW TRANSMITTER
GENERAL |  | 1 | Tag Number |  | Description |  |  |  |  | See Page 14 of 26 |  | See Page 14 of 26
|  | 2 | Service | [6 empty] | See Page 14 of 26
|  | 3 | Quantity | [6 empty] | See Page 14 of 26
|  | 4 | P&ID No. |  | Area Classification |  |  |  |  | See Page 14 of 26 |  |  | Unclassified Area
ELECTRONICS |  | 5 | Type |  | Processors |  |  |  |  | Digital |  |  | Microproccesors
|  | 6 | Software |  | Programing |  |  |  |  | MFR STD |  |  | Local Hand Held Device
|  | 7 | Serial Interface |  | Comn Protocol |  |  |  |  | No |  |  | HART Smart
Process Condition |  | 8 | Fluid | [6 empty] | water
|  | 9 | Temperature |  | Min. |  | Oper. |  | Max. | See Page 14 of 26 |  |  |  | °C
|  | 10 | Pressure |  | Min. |  | Oper. |  | Max. | See Page 14 of 26 |  |  |  | kPa
|  | 11 | Flowrate |  | Min. |  | Oper. |  | Max. | See Page 14 of 26 |  |  |  | m3/h
|  | 12 | Velocity |  | Min. |  | Oper. |  | Max. | 0 | 4.5 |  |  | m/s
|  | 13 | Conductivity |  | Min. |  | Oper. |  | Max. | 0 | >20 |  |  | µS/CM
14
|  | 15 | Fluid state | [6 empty] | Liquid
ELEMENT |  | 16 | Type | [6 empty] | see page 14, note 2
|  | 17 | End Connection | Size | [5 empty] | See Page 14 of 26
|  | 18 |  | Rating | [5 empty] | JIS 10K
|  | 17 | Electrode | Size | [5 empty] | MFR
|  | 18 |  | Material | [5 empty] | 316 L SS for soften water and MFR for sea water
|  | 19 | Enclosure Protection Rating | [6 empty] | IP54
|  | 20 | Area Class | [6 empty] | Non-Hazardous area
|  | 21 | Power Supply | [6 empty] | 220 VAC
Transmitter |  | 22 | Type |  | Mounting |  |  |  |  | Smart Hart |  |  | Remote Mounted
|  | 23 | Sensor Type |  | Connection to Well |  |  |  |  | TBA
|  | 24 | Housing |  | Painting |  |  |  |  | Low Cooper Cast Aluminium Alloy with Anti-Corrosion Coating |  |  | MFR STD
|  | 25 | Power Supply |  | Load Resistance |  |  |  |  | 220 VAC |  |  | MFR STD
|  | 26 | Electrical Connection |  | Input |  |  | Output |  | 1/2" NPTF |  |  | 1/2" NPTF
|  | 27 | Accuracy |  | Calibration |  |  |  |  | ± 1% Of Span
|  | 28 | Integral Meter |  | Scale |  |  |  |  | Yes, LCD |  |  | TBA
|  | 29 | Instrument Range |  | Min. |  |  | Max. |  | See Page 14 of 26
|  | 30 | Calibration Range |  | Min. |  |  | Max. |  | TBA
|  | 31 | Options | [6 empty] | -
|  | 32 | Electrical Class | [6 empty] | N/A
Communication and Software |  | 33 | Communication Type | [6 empty] | 4-20 mA + HART |  |  | Conventional
|  | 34 | D D Revision | [6 empty] | Latest Revision
|  | 35 | Hart Descriptor
|  | 36 | Internal Diagnostics | [6 empty] | YES
Purchase |  | 39 | Vendor | [6 empty] | TBA
|  | 40 | Manufacture |  |  | Model |  |  |  | TBA |  |  | TBA
|  | 41 | Po No. | [6 empty] | TBA
Notes :
1. Refer to General Instrument Specification P3FH-IN-9000-SPE-1001
2. Flow Tube c/w built-in grounding 316 SST Electrodes and Empty pipe detection 316 SST Electrodes (magnetic flow meter)
3. Remote Programing by Handheld Programer (Hart Com) or By Computer with Vendor Software
4. Vendor shall submit detail drawing with spesification
5. Vendor shall provide and attach SS nameplate